{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["정수","원수","라돈"],"not_rendered":{"defined_names":2},"read":"whole","date_system":"1900"}

{"sheet":"정수","index":0,"n_rows":42,"n_cols":66,"rows_kept":42}
["연번","채수일자","출력일","채수장소","결과","부적합항목","일반세균","총대장균군","납","불소","비소","셀레늄","수은","시안","크롬","암모니아성질소","질산성질소","카드뮴","페놀","총트리할로메탄","다이아지논","파라티온","1,2-디브로모-3-클로로프로판","페니트로티온","카바릴","1,1,1-트리클로로에탄","테트라클로로에틸렌","트리클로로에틸렌","디클로로메탄","벤젠","톨루엔","에틸벤젠","크실렌","1,1-디클로로에틸렌","사염화탄소","경도","과망간산칼륨소비량","냄새","맛","동","색도","세제(음이온계면활성제)","수소이온농도","아연","염소이온","증발잔류물","철","망간","탁도","황산이온","알루미늄","잔류염소","붕소","클로로포름","대장균","클로랄하이드레이트","디브로모아세토니트릴","디클로로아세토니트릴","트리클로로아세토니트릴","할로아세틱에시드","브로모디클로로메탄","디브로모클로로메탄","1,4-다이옥산","포름알데히드","브롬산염","우라늄"]
[1,"2023-06-27","2023-07-04","율촌 송도 정수","부적합","탁도",13,"불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 3.4"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 33"," 3.0"," 무취"," 무미"," 0.011"," 불검출"," 불검출"," 7.3"," 0.164"," 9.5"," 117"," 0.077"," 불검출",2.03," 9"," 0.08"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0001"]
[2,"2023-06-23","2023-06-28","주삼 고막 정수","적합",null," 1","불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 1.6"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 110"," 1.1"," 무취"," 무미"," 0.004"," 불검출"," 불검출"," 7.1"," 0.029"," 12.4"," 203"," 0.123"," 불검출"," 0.23"," 16"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0012"]
[3,"2023-05-23","2023-06-16","남면 연도 정수","적합",""," 0"," 불검출"," 불검출"," 0.71"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.005"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 98"," 0.6"," 무취"," 무미"," 0.004"," 불검출"," 불검출"," 7.1"," 0.011"," 28.0"," 219"," 0.151"," 불검출"," 0.47"," 51"," 불검출"," 0.70"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0005"," 불검출"," 불검출"," 0.012"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0031"," 0.0002"]
[4,"2023-05-23","2023-06-16","남면 횡간 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.024"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 13"," 0.5"," 무취"," 무미"," 0.010"," 불검출"," 불검출"," 7.0"," 0.012"," 14.8"," 83"," 불검출"," 불검출"," 0.29"," 4"," 0.03"," 0.40"," 불검출"," 0.008"," 불검출"," 0.0028"," 0.0009"," 불검출"," 불검출"," 0.015"," 0.009"," 0.006"," 불검출"," 불검출"," 불검출"," 불검출"]
[5,"2023-05-23","2023-06-16","남면 부도 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.013"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 10"," 0.4"," 무취"," 무미"," 0.010"," 불검출"," 불검출"," 7.0"," 0.011"," 14.5"," 73"," 불검출"," 불검출"," 0.29"," 4"," 0.03"," 0.60"," 불검출"," 0.005"," 불검출"," 0.0016"," 0.0008"," 불검출"," 불검출"," 0.012"," 0.004"," 불검출"," 불검출"," 불검출"," 0.0008"," 불검출"]
[6,"2023-05-23","2023-06-16","남면 나발 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.021"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 13"," 0.4"," 무취"," 무미"," 0.012"," 불검출"," 불검출"," 6.8"," 0.012"," 15.9"," 20"," 불검출"," 불검출"," 0.29"," 4"," 0.03"," 0.60"," 불검출"," 0.007"," 불검출"," 0.0020"," 0.0007"," 불검출"," 불검출"," 0.017"," 0.008"," 0.005"," 불검출"," 불검출"," 0.0010"," 불검출"]
[7,"2023-05-23","2023-06-16","남면 소두라 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.026"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 13"," 0.4"," 무취"," 무미"," 0.013"," 불검출"," 불검출"," 6.7"," 0.049"," 15.4"," 48"," 불검출"," 불검출"," 0.32"," 4"," 0.03"," 0.70"," 불검출"," 0.010"," 불검출"," 0.0019"," 0.0009"," 불검출"," 불검출"," 0.006"," 0.008"," 0.006"," 불검출"," 불검출"," 0.0005"," 불검출"]
[8,"2023-05-23","2023-06-16","남면 선창 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.037"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 19"," 0.3"," 무취"," 무미"," 0.010"," 불검출"," 불검출"," 7.1"," 0.025"," 18.3"," 109"," 불검출"," 불검출"," 0.29"," 4"," 0.03"," 0.70"," 불검출"," 0.017"," 불검출"," 0.0016"," 0.0009"," 불검출"," 불검출"," 0.015"," 0.011"," 0.007"," 불검출"," 불검출"," 0.0014"," 불검출"]
[9,"2023-05-23","2023-06-16","남면 봉통 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.031"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 14"," 0.3"," 무취"," 무미"," 0.008"," 불검출"," 불검출"," 6.9"," 0.010"," 16.3"," 24"," 불검출"," 불검출"," 0.28"," 4"," 0.03"," 1.00"," 불검출"," 0.013"," 불검출"," 0.0013"," 0.0005"," 불검출"," 불검출"," 0.017"," 0.011"," 0.006"," 불검출"," 불검출"," 0.0006"," 불검출"]
[10,"2023-05-23","2023-06-16","남면 대두 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.020"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 13"," 0.5"," 무취"," 무미"," 0.010"," 불검출"," 불검출"," 6.8"," 0.018"," 15.0"," 57"," 불검출"," 불검출"," 0.30"," 4"," 0.03"," 0.80"," 불검출"," 0.008"," 불검출"," 0.0018"," 0.0008"," 불검출"," 불검출"," 0.015"," 0.007"," 0.004"," 불검출"," 불검출"," 불검출"," 불검출"]
[11,"2023-05-23","2023-06-16","남면 소횡간 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.015"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 14"," 0.3"," 무취"," 무미"," 0.008"," 불검출"," 불검출"," 6.8"," 0.014"," 15.4"," 51"," 불검출"," 불검출"," 0.29"," 4"," 0.03"," 0.60"," 불검출"," 0.006"," 불검출"," 0.0018"," 0.0007"," 불검출"," 불검출"," 0.012"," 0.005"," 불검출"," 불검출"," 불검출"," 0.0005"," 불검출"]
[12,"2023-05-23","2023-06-16","화정 월호 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.8"," 불검출"," 불검출"," 0.022"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 29"," 3.3"," 무취"," 무미"," 0.006"," 불검출"," 불검출"," 6.7"," 0.013"," 10.6"," 63"," 불검출"," 불검출"," 0.31"," 6"," 0.02"," 불검출"," 불검출"," 0.013"," 불검출"," 0.0017"," 불검출"," 0.0010"," 불검출"," 0.009"," 0.006"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[13,"2023-05-23","2023-06-16","화정 여자 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.8"," 불검출"," 불검출"," 0.023"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 27"," 3.0"," 무취"," 무미"," 0.008"," 불검출"," 불검출"," 6.7"," 0.027"," 10.6"," 72"," 불검출"," 불검출"," 0.26"," 6"," 0.02"," 불검출"," 불검출"," 0.013"," 불검출"," 0.0018"," 불검출"," 0.0008"," 불검출"," 0.011"," 0.006"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[14,"2023-05-23","2023-06-16","화정 상화 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.5"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 6.7"," 불검출"," 0.4"," 53"," 불검출"," 불검출"," 0.06"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[15,"2023-05-23","2023-06-16","화정 자봉 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.8"," 불검출"," 불검출"," 0.025"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 30"," 2.3"," 무취"," 무미"," 0.010"," 불검출"," 불검출"," 6.7"," 0.038"," 10.6"," 68"," 불검출"," 불검출"," 0.20"," 6"," 불검출"," 불검출"," 불검출"," 0.015"," 불검출"," 0.0016"," 불검출"," 0.0008"," 불검출"," 0.009"," 0.007"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[16,"2023-05-23","2023-06-16","화정 하화 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.8"," 불검출"," 불검출"," 0.021"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 32"," 2.9"," 무취"," 무미"," 0.007"," 불검출"," 불검출"," 6.9"," 0.018"," 10.6"," 26"," 불검출"," 불검출"," 0.27"," 6"," 0.02"," 불검출"," 불검출"," 0.012"," 불검출"," 0.0016"," 불검출"," 0.0008"," 불검출"," 0.009"," 0.006"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[17,"2023-05-23","2023-06-16","화정 송여자 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.8"," 불검출"," 불검출"," 0.021"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 30"," 2.3"," 무취"," 무미"," 0.013"," 불검출"," 불검출"," 6.7"," 0.070"," 10.6"," 57"," 불검출"," 불검출"," 0.16"," 6"," 불검출"," 불검출"," 불검출"," 0.012"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.003"," 0.006"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[18,"2023-05-23","2023-06-16","화정 제도 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 1.0"," 불검출"," 불검출"," 0.012"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 31"," 1.8"," 무취"," 무미"," 0.005"," 불검출"," 불검출"," 6.6"," 0.031"," 11.5"," 23"," 불검출"," 불검출"," 0.32"," 7"," 0.02"," 불검출"," 불검출"," 0.007"," 불검출"," 0.0017"," 불검출"," 0.0008"," 불검출"," 0.010"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"]
[19,"2023-05-23","2023-06-16","돌산 금죽 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.4"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 57"," 0.4"," 무취"," 무미"," 0.006"," 불검출"," 불검출"," 6.4"," 1.958"," 24.8"," 141"," 0.059"," 불검출"," 0.34"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0029"," 0.0001"]
[20,"2023-05-25","2023-06-16","삼산 죽촌 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 3.5"," 불검출"," 불검출"," 0.016"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 45"," 3.2"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 6.5"," 0.012"," 59.1"," 181"," 불검출"," 불검출"," 0.11"," 8"," 불검출"," 0.60"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0036"," 불검출"," 불검출"," 0.020"," 불검출"," 0.006"," 불검출"," 불검출"," 불검출",""]
[21,"2023-05-25","2023-06-16","삼산 대동 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 2.9"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 66"," 3.3"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 6.8"," 0.147"," 46.8"," 199"," 0.061"," 불검출"," 0.30"," 16"," 불검출"," 0.20"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0001"]
[22,"2023-05-25","2023-06-16","삼산 의성 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.5"," 불검출"," 불검출"," 0.023"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.003"," 불검출"," 불검출"," 불검출"," 불검출"," 52"," 2.7"," 무취"," 무미"," 0.007"," 불검출"," 불검출"," 6.7"," 0.046"," 27.3"," 145"," 불검출"," 불검출"," 0.28"," 4"," 불검출"," 0.60"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0007"," 불검출"," 불검출"," 0.015"," 불검출"," 0.010"," 불검출"," 불검출"," 불검출"," 0.0001"]
[23,"2023-05-25","2023-06-16","삼산 진막 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.018"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 41"," 1.3"," 무취"," 무미"," 0.013"," 불검출"," 불검출"," 6.7"," 0.034"," 24.5"," 103"," 불검출"," 불검출"," 0.13"," 6"," 불검출"," 0.70"," 불검출"," 0.005"," 불검출"," 불검출"," 0.0008"," 불검출"," 불검출"," 0.006"," 0.006"," 0.005"," 불검출"," 불검출"," 불검출"," 불검출"]
[24,"2023-05-25","2023-06-16","삼산 손죽 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.9"," 불검출"," 불검출"," 0.030"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 43"," 1.4"," 무취"," 무미"," 0.015"," 불검출"," 불검출"," 6.6"," 0.103"," 40.0"," 162"," 0.076"," 불검출"," 0.48"," 12"," 0.04"," 0.60"," 불검출"," 0.003"," 불검출"," 불검출"," 0.0020"," 불검출"," 불검출"," 0.010"," 0.008"," 0.012"," 불검출"," 불검출"," 불검출"," 0.0002"]
[25,"2023-05-25","2023-06-16","삼산 유촌 정수","적합",""," 3"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 1.7"," 불검출"," 불검출"," 0.025"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 43"," 3.3"," 무취"," 무미"," 0.018"," 불검출"," 불검출"," 6.7"," 0.140"," 69.8"," 11"," 0.082"," 불검출"," 0.40"," 9"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0016"," 불검출"," 불검출"," 0.019"," 0.005"," 0.010"," 불검출"," 불검출"," 불검출"," 불검출"]
[26,"2023-05-25","2023-06-16","삼산 초도 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 3.3"," 불검출"," 불검출"," 0.011"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 72"," 0.4"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 6.5"," 0.051"," 50.6"," 118"," 0.062"," 불검출"," 0.28"," 18"," 불검출"," 0.60"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.021"," 불검출"," 0.004"," 불검출"," 불검출"," 불검출",""]
[27,"2023-06-27","2023-07-04","삼산 예미 정수","부적합","염소이온"," 0"," 불검출"," 불검출"," 0.16"," 0.006"," 0.0090"," 불검출"," 불검출"," 불검출"," 불검출"," 1.3",0.005," 불검출"," 0.014"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출",248," 3.2"," 무취"," 무미"," 0.006"," 불검출"," 불검출"," 6.6"," 0.307",284.8," 459",0.229," 불검출"," 0.14"," 78"," 불검출"," 0.80"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.068"," 불검출"," 불검출"," 불검출"," 불검출",0.0083," 불검출"]
[28,"2023-05-25","2023-06-16","삼산 소거문 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 1.5"," 불검출"," 불검출"," 0.021"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 49"," 0.7"," 무취"," 무미"," 0.019"," 불검출"," 불검출"," 6.6"," 0.226"," 41.8"," 324"," 0.052"," 불검출"," 0.14"," 10"," 불검출"," 0.80"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0014"," 불검출"," 불검출"," 0.014"," 0.005"," 0.008"," 불검출"," 불검출"," 0.0006"," 0.0005"]
[29,"2023-05-25","2023-06-16","삼산 평도 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 2.7"," 불검출"," 불검출"," 0.033"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 73"," 1.2"," 무취"," 무미"," 0.008"," 불검출"," 불검출"," 6.7"," 0.032"," 123.7"," 87"," 불검출"," 불검출"," 0.45"," 25"," 불검출"," 0.80"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0022"," 불검출"," 불검출"," 0.017"," 불검출"," 0.010"," 불검출"," 불검출"," 0.0010"," 불검출"]
[30,"2023-05-25","2023-06-16","삼산 광도 정수","적합",""," 1"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.1"," 불검출"," 불검출"," 0.028"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 불검출"," 불검출"," 42"," 2.7"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 6.6"," 0.075"," 70.8"," 37"," 불검출"," 불검출"," 0.19"," 13"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0026"," 불검출"," 불검출"," 0.011"," 0.004"," 0.011"," 불검출"," 불검출"," 불검출",""]
[31,"2023-06-23","2023-06-28","화양 오천 정수","부적합","일반세균,총대장균군",160," 검출"," 불검출"," 0.28"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 4.3"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 62"," 1.1"," 무취"," 무미"," 0.006"," 불검출"," 불검출"," 8.0"," 0.005"," 43.9"," 221"," 0.204"," 0.008"," 0.23"," 32"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 0.0002"]
[32,"2023-06-23","2023-06-28","화양 장등 정수","부적합","질산성질소"," 9"," 불검출"," 불검출"," 0.16"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출",10.5," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 52"," 0.4"," 무취"," 무미"," 0.005"," 불검출"," 불검출"," 8.0"," 0.008"," 17.9"," 105"," 0.070"," 0.005"," 0.06"," 12"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0002"]
[33,"2023-06-23","2023-06-28","화양 대서이 정수","부적합","일반세균,총대장균군",130," 검출"," 불검출"," 0.79"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.5"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 15"," 0.4"," 무취"," 무미"," 0.004"," 불검출"," 불검출"," 8.0"," 0.025"," 16.0"," 357"," 0.067"," 0.005"," 0.06"," 16"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0003"]
[34,"2023-06-23","2023-06-28","화양 운두 정수","적합",null,0,"불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 75"," 0.3"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 8.1"," 0.023"," 17.3"," 47"," 불검출"," 0.005"," 0.11"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0001"]
[35,"2023-06-23","2023-06-28","화양 장수 정수","적합",null,0," 불검출"," 불검출"," 0.22"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 4.9"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 77"," 0.3"," 무취"," 무미"," 불검출"," 불검출"," 불검출"," 7.6"," 0.008"," 16.4"," 298"," 0.095"," 0.005"," 0.06"," 10"," 불검출"," 0.40"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.002"," 불검출"," 불검출"," 0.0005"]
[36,"2023-05-23","2023-06-16","화양 공정 정수","적합",""," 0"," 불검출"," 불검출"," 0.19"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 4.9"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 85"," 0.8"," 무취"," 무미"," 0.006"," 불검출"," 불검출"," 7.5"," 0.025"," 16.3"," 297"," 0.099"," 0.005"," 0.10"," 10"," 불검출"," 1.00"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.001"," 불검출"," 불검출"," 0.0005"]
[37,"2023-05-26","2023-06-16","화양 장척 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 8.4"," 불검출"," 불검출"," 0.005"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 94"," 0.7"," 무취"," 무미"," 0.009"," 불검출"," 불검출"," 7.5"," 0.019"," 20.2"," 445"," 0.101"," 0.005"," 0.04"," 16"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0015"," 0.0003"]
[38,"2023-05-23","2023-06-16","화양 창무 정수","적합",""," 0"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0051"," 불검출"," 불검출"," 불검출"," 불검출"," 2.8"," 불검출"," 불검출"," 0.025"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 142"," 0.5"," 무취"," 무미"," 불검출"," 불검출"," 0.1"," 8.1"," 불검출"," 41.5"," 305"," 0.237"," 0.005"," 0.41"," 20"," 불검출"," 불검출"," 불검출"," 0.016"," 불검출"," 0.0193"," 0.0008"," 불검출"," 불검출"," 0.045"," 0.006"," 불검출"," 불검출"," 0.02"," 0.0088"," 0.0002"]
[39,"2023-05-26","2023-06-16","소라 하의곡 정수","적합",""," 0"," 불검출"," 불검출"," 0.16"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 2.2"," 불검출"," 불검출"," 0.005"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 88"," 0.6"," 무취"," 무미"," 0.005"," 불검출"," 불검출"," 7.4"," 0.007"," 10.1"," 259"," 0.150"," 0.005"," 0.06"," 26"," 불검출"," 0.20"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0005"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0007"]
[40,"2023-05-26","2023-06-16","소라 상의곡 정수","적합",""," 1"," 불검출"," 불검출"," 0.18"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 2.2"," 불검출"," 불검출"," 0.004"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 89"," 0.7"," 무취"," 무미"," 0.005"," 불검출"," 불검출"," 7.2"," 0.006"," 9.9"," 219"," 0.140"," 0.005"," 0.07"," 26"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0007"]
[41,"2023-05-26","2023-06-16","돌산 월암 정수","적합",""," 0"," 불검출"," 불검출"," 0.38"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 4.3"," 불검출"," 불검출"," 0.003"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 66"," 0.4"," 무취"," 무미"," 0.007"," 불검출"," 불검출"," 7.1"," 0.013"," 16.9"," 49"," 0.094"," 0.005"," 0.05"," 7"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 불검출"," 0.0011"," 0.0011"]

{"sheet":"원수","index":1,"n_rows":5,"n_cols":11,"rows_kept":5}
["연번","채수일자","출력일","채수장소","결과","수소이온농도","생물화학적산소요구량","부유물질량","용존산소량","총대장균군","분원성대장균군"]
[1,"2023-05-25","2023-06-16","삼산 죽촌 원수","적합","6.7"," 0.3"," 1.4"," 9.2"," 49"," 49"]
[2,"2023-05-25","2023-06-16","삼산 손죽 원수","적합","6.6"," 0.2"," 2.4"," 9.2"," 불검출"," 불검출"]
[3,"2023-05-25","2023-06-16","삼산 초도 원수","적합","6.4"," 0.2"," 1.4"," 9.3"," 불검출"," 불검출"]
[4,"2023-05-25","2023-06-16","삼산 광도 원수","적합","6.6"," 0.3"," 1.2"," 9.1"," 79"," 22"]

{"sheet":"라돈","index":2,"n_rows":39,"n_cols":6,"rows_kept":39}
["연번","채수일자","출력일","채수장소","결과","라돈"]
[1,"2023-05-19","2023-06-16","율촌 송도 정수","적합"," 불검출"]
[2,"2023-05-19","2023-06-16","주삼 고막 정수","적합"," 불검출"]
[3,"2023-05-23","2023-06-16","남면 연도 정수","적합"," 불검출"]
[4,"2023-05-23","2023-06-16","남면 횡간 정수","적합"," 불검출"]
[5,"2023-05-23","2023-06-16","남면 부도 정수","적합"," 불검출"]
[6,"2023-05-23","2023-06-16","남면 나발 정수","적합"," 불검출"]
[7,"2023-05-23","2023-06-16","남면 소두라 정수","적합"," 불검출"]
[8,"2023-05-23","2023-06-16","남면 선창 정수","적합"," 불검출"]
[9,"2023-05-23","2023-06-16","남면 봉통 정수","적합"," 불검출"]
[10,"2023-05-23","2023-06-16","남면 대두 정수","적합"," 불검출"]
[11,"2023-05-23","2023-06-16","남면 소횡간 정수","적합"," 불검출"]
[12,"2023-05-23","2023-06-16","화정 월호 정수","적합"," 불검출"]
[13,"2023-05-23","2023-06-16","화정 여자 정수","적합"," 불검출"]
[14,"2023-05-23","2023-06-16","화정 상화 정수","적합"," 불검출"]
[15,"2023-05-23","2023-06-16","화정 자봉 정수","적합"," 불검출"]
[16,"2023-05-23","2023-06-16","화정 하화 정수","적합"," 불검출"]
[17,"2023-05-23","2023-06-16","화정 송여자 정수","적합"," 불검출"]
[18,"2023-05-23","2023-06-16","화정 제도 정수","적합"," 불검출"]
[19,"2023-05-23","2023-06-16","돌산 금죽 정수","적합"," 불검출"]
[20,"2023-05-25","2023-06-16","삼산 대동 정수","적합"," 불검출"]
[21,"2023-05-25","2023-06-16","삼산 의성 정수","적합"," 불검출"]
[22,"2023-05-25","2023-06-16","삼산 진막 정수","적합"," 불검출"]
[23,"2023-05-25","2023-06-16","삼산 손죽 정수","적합"," 불검출"]
[24,"2023-05-25","2023-06-16","삼산 유촌 정수","적합"," 불검출"]
[25,"2023-05-25","2023-06-16","삼산 예미 정수","적합"," 5.5"]
[26,"2023-05-25","2023-06-16","삼산 소거문 정수","적합"," 불검출"]
[27,"2023-05-25","2023-06-16","삼산 평도 정수","적합"," 불검출"]
[28,"2023-05-24","2023-06-16","화양 오천 정수","적합"," 불검출"]
[29,"2023-05-24","2023-06-16","화양 장등 정수","적합"," 불검출"]
[30,"2023-05-24","2023-06-16","화양 대서이 정수","적합"," 불검출"]
[31,"2023-05-26","2023-06-16","화양 운두 정수","적합"," 불검출"]
[32,"2023-05-23","2023-06-16","화양 장수 정수","적합"," 불검출"]
[33,"2023-05-23","2023-06-16","화양 공정 정수","적합"," 불검출"]
[34,"2023-05-26","2023-06-16","화양 장척 정수","적합"," 불검출"]
[35,"2023-05-23","2023-06-16","화양 창무 정수","적합"," 불검출"]
[36,"2023-05-26","2023-06-16","소라 하의곡 정수","적합"," 20.6"]
[37,"2023-05-26","2023-06-16","소라 상의곡 정수","적합"," 22.3"]
[38,"2023-05-26","2023-06-16","돌산 월암 정수","적합"," 25.2"]